OFFICE NOTE

Sub: Emergency procurement of 132 kV station-class polymer Lightning Arresters                        (6 Nos.) for 132/33 kV SS Pamarru, OMC Circle, Vijayawada — Approval — Reg.

Ref: 1. AEE/SS/Pamarru, Lr. No. AEE/IBP/SS/LA/34/2025, dt. 28-10-2025

2. MRT Division test report, MRT/RR/TR-211/2025, dt. 29-10-2025.

3. EE/Construction/_____ email dt. 29-10-2025 regarding inter-diversion

feasibility.

- - -

- Purpose:

To seek approval for emergency procurement of 6 Nos. 132 kV station-class polymer lightning arresters (rated 120 kV MCOV, 10 kA) for 132/33 kV Sub-Station Pamarru, under the emergency procurement provisions of APTRANSCO Delegation of Financial Powers, to ensure bay protection before the Northeast monsoon activity.

- Facts/Chronology:

2.1 On 27-10-2025, three LAs on the 132 kV incoming bay-2 and three LAs on the 132 kV bus section-2 showed IR < 10 MΩ; porcelain hairline cracks observed (Ref-1).

2.2 MRT tests on 29-10-2025 confirmed leakage current > 1.2 mA at reference voltage; visual tracking marks present (Ref-2).

2.3 EE/Construction examined inter-diversion from nearby stores; no spare stock of 132 kV station-class LAs available (Ref-3).

2.4 Forecast indicates thunderstorm activity in November 2025, elevating risk to PTRs/bays if LAs remain defective.

- Issues for decision:

3.1 Whether to approve emergency procurement of 6 Nos. 132 kV LAs for immediate replacement at SS Pamarru.

3.2 Whether to permit single-tender/limited enquiry citing urgency, with post-facto ratification as per Delegation.

- Rules/Authority:

- APTRANSCO Delegation of Financial Powers (latest amendment) — emergency procurement for system protection.

- Grid Code obligations on maintaining protection systems.

- Standard Procurement Guidelines on limited enquiry in urgent safety cases.

- Analysis:

- Option A — Repair/continue in service: Not recommended; IR and leakage current outside limits; risk of surge failure and transformer/bay damage.

- Option B — Inter-divert from nearby stores: Not feasible; no stock available (Ref-3).

- Option C — Procure 6 Nos. new LAs via limited enquiry (3 registered vendors), 7-day delivery: Recommended; mitigates immediate risk and meets monsoon timeline.

- Technical requirement: 132 kV station-class polymer LA, 10 kA, 120 kV MCOV, IEC/IS compliant, with clamps, nameplate, and test certificates.

- Estimated unit cost: Rs.1,35,000 (recent buys); Total: Rs.8,10,000 + GST; say Rs.9,55,800 (incl. GST @18%).

- Risk if delayed: PTR/Bay insulation stress; unplanned outages; potential high-value asset damage.

- Financials/Safety/Timeline:

- Head of Account: O&M — Sub-station Consumables/Protection (FY 2025-26).

- Availability: Within sanctioned O&M budget (current unspent provision Rs.18 lakh).

- Safety: Replacement under approved SOP with PTW/LOTO, earthing verified; barricading during shutdown.

- Timeline:

  - RFQ to 3 vetted vendors: 31-10-2025

  - Bid close & L1 determination: 02-11-2025

  - Supply to site: by 06-11-2025

  - Installation & testing: 07–08-11-2025 (two 3-hr shutdowns)

- Proposal:

Approve Option C — procurement of 6 Nos. 132 kV station-class polymer LAs for SS Pamarru at an estimated cost of Rs.9,55,800 (incl. GST) under O&M budget, through limited enquiry to three approved vendors invoking emergency provisions; SE/Operation, Rangareddy to issue RFQ, place order on L1, and ensure installation by 08-11-2025. Post-facto ratification to be placed before competent authority in the next review.

- Draft Order/Letter enclosed at Flag ‘X’ for signature.

Submitted for kind approval, please.

Superintending Engineer