TRANSMISSION CORPORATION OF ANDHRA PRADESH LIMITED
VIDYUT SOUDHA :: VIJAYAWADA

Memo No. Estt/___/2025  Date: ..2025

Sub: APTRANSCO – Establishment – Disciplinary case against Sri ____________, AEE/220 kV __________ SS – Failure to ensure removal of portable earth prior to restoration resulting in REF operation of 220/132 kV PTR–2 on 25.01.2025 at 06:14 hrs – Proposal for minor penalty – Final orders – Issued.

Ref:

- Incident report dated 25.01.2025 of AEE/220 kV _________ SS regarding tripping of 220/132 kV PTR–2 on 64 REF with 86T lockout.

- Note dated 27.01.2025 of DE/Operation, __________ Division.

- Memo No. Estt/Discip/SCN-Minor/___/2025, dated ..2025, issued to Sri ____________, AEE/220 kV _________ SS.

- Written explanation dated ..2025 submitted by Sri ____________, AEE/220 kV _________ SS.

In continuation of the references cited, the disciplinary case against Sri ____________, AEE/220 kV _________ SS, is examined and final orders are issued as below:

Speaking order Technical_Minor …

### 1) Facts & Proceedings

- At the relevant time, Sri ____________ was working as AEE/220 kV _________ SS and was the shift in-charge responsible for observing all safety procedures, including application and removal of portable earths and adherence to LOTO / operating instructions during shutdown and restoration.

- On 25.01.2025 at 06:14 hrs, during restoration of 132 kV Bus–B at 220 kV _________ SS, 220/132 kV PTR–2 tripped on 64 REF with 86T lockout on first energisation attempt. Supply was restored at about 07:45 hrs after checks, with no damage to equipment.

- During post-incident checks, one portable earthing rod was found still connected on the 132 kV Bus–B bay earthing point under barricading, indicating incomplete de-earthing at the time of energisation. DR/SSR traces confirmed REF operation corresponding to an external earth path.

- The note dated 27.01.2025 of DE/Operation recorded that (i) de-earthing was incomplete; (ii) the Earthing / LOTO checklist did not contain the mandatory second-person cross-verification; and (iii) the shift logbook showed that restoration was authorised by Sri ____________, AEE/220 kV _________ SS, as shift in-charge.

- In view of the above, Show Cause Notice in the reference 3rd cited was issued to Sri ____________, AEE/220 kV _________ SS, proposing minor penalty under the A.P.S.E.B. Employees’ Discipline & Appeal Regulations (as adopted by APTRANSCO), alleging negligence / dereliction of duty in not ensuring complete de-earthing and checklist compliance before authorising energisation.

- In his written explanation (ref.4), Sri ____________ contended, inter alia, that:
(a) the portable earth was applied by previous shift staff;
(b) shift changeover was in progress;
(c) SCADA indication showed readiness;
(d) there was no damage to equipment and supply was restored promptly;
(e) the lapse, if any, was collective and not solely attributable to him.

- The records of incident, DR/SSR data, checklists, logbooks and the explanation of Sri ____________ have been carefully examined by the Disciplinary Authority.

### 2) Findings with Reasons

- As shift in-charge at the material time, Sri ____________ had a clear, non-delegable responsibility to ensure:
(i) completion of de-earthing;
(ii) compliance of two-person verification and checklist; and
(iii) physical confirmation of removal of all portable earths, before authorising charging of 132 kV Bus–B.

- The DR/SSR traces and post-incident verification conclusively establish that a portable earthing rod remained connected on 132 kV Bus–B earthing point at the time of energisation, which constituted an avoidable external earth path leading to 64 REF operation of PTR–2. This evidences lapse in ensuring complete de-earthing.

- The Earthing / LOTO checklist lacked the mandatory second-person sign-off and the logbook indicates that energisation was authorised by Sri ____________, AEE. This clearly shows non-compliance with the prescribed Station Operating Procedures.

- The contentions of Sri ____________ that the lapse was collective, that SCADA showed “ready”, and that no damage occurred, do not absolve him of responsibility:

  - SCADA / remote indications are only supplementary and cannot replace physical verification mandated under safety procedures.

  - Shift in-charge is required to personally ensure observance of all safety checks before issuing closing instructions.

  - Absence of equipment damage or prolonged outage may be a mitigating factor in assessing quantum of penalty, but does not erase the established negligence.

- There is no material on record to indicate any mala fide intention or personal gain. The lapse is, however, a serious deviation from safety discipline which could have resulted in major equipment damage and risk to personnel.

Finding: The charge that Sri ____________, AEE/220 kV _________ SS, failed to ensure complete de-earthing and checklist compliance before authorising energisation, resulting in a preventable REF trip of PTR–2, is held proved. The said lapse amounts to negligence and lack of due care in discharge of duties, attracting minor penalty under the A.P.S.E.B. Employees’ Discipline & Appeal Regulations (as adopted by APTRANSCO).

### 3) Order

- Considering the nature of lapse, its potential risk, the fact that no equipment damage occurred, and there is no evidence of mala fide intention, the Disciplinary Authority is of the view that imposition of a minor penalty will meet the ends of justice.

- Accordingly, in exercise of powers conferred under the A.P.S.E.B. Employees’ Discipline & Appeal Regulations, as adopted by APTRANSCO, the undersigned hereby imposes on Sri ____________, AEE/220 kV _________ SS, the penalty of:

“Withholding of ONE (1) annual grade increment without cumulative effect.”

- The above penalty shall:
(i) take effect from the next due date of annual grade increment following service of this memo;
(ii) not have cumulative effect; and
(iii) be recorded in the Service Register of the individual as a minor penalty under the said Regulations.

- Sri ____________, AEE/220 kV _________ SS, is advised to exercise utmost care hereafter in adhering to safety codes, LOTO / earthing procedures and operating instructions. Any recurrence of such lapses will be viewed seriously.

### 4) Right of Appeal

- Sri ____________, AEE/220 kV _________ SS, may prefer an appeal, if so advised, to the Competent Appellate Authority under the A.P.S.E.B. Employees’ Discipline & Appeal Regulations (as adopted by APTRANSCO) within 45 (forty-five) days from the date of receipt of this memo.

(Signature)
[Name]
[Designation of Disciplinary Authority]
APTRANSCO

To
Sri ____________,
AEE/220 kV _________ SS,
APTRANSCO.

Copy to:

- The Chief Engineer/__________, APTRANSCO.

- The Superintending Engineer/__________, APTRANSCO.

- The DE/Operation, __________ Division – for serving the memo on Sri ____________, AEE, obtaining dated acknowledgement on the duplicate and returning the same to this office.

- AO/Estt., O/o __________ – for regulating pay and noting in Service Register.

- Stock file.

Sources